## Panel schedule — MDP-1
Panel schedule — MDP-1
generated 2026-06-11T20:42:38
Panel identity
Name | MDP-1
Manufacturer | Square D
Model | TBD
Voltage | 480/277V
Phase | 3
Wire | TBD
Mains rating (A) | 800
Fed from | TBD
Verified | VERIFIED
Location
Room | TBD
Zone | TBD
Notes
Notes | Cover label reads "MDP-1 277/480 VOLT". Main breaker nameplate (Square D HCW): cat HCW1F05435-1B (cat # read from photo; not yet datasheet-confirmed), 800 A, 480 V, 3 PH, WIRE = 3 (per nameplate). My earlier note that "WIRE = 3 means 3 conductors through the breaker and the system is 4-wire" was an INTERPRETATION, not verified. Field-verify the system wire count by opening the cabinet and checking for a neutral bar. Panel has TWO label sets: older engraved black nameplates (e.g. SOAP PUMP #1, TANK #3 HEAT, AC PUMP, MILL #2 AIR COMP., EPR-1) and newer orange labels with -P# suffixes (e.g. SOAP PUMP 1 - P7, RACK 1 PUMP - P3, PRODUCTION PUMP - P2, EPR-1 PUMP - P11). Both kept in breaker notes. Three orange labels not yet tied to a position: PRODUCTION PUMP - P2, MILL/M11 AIR COMPRESSOR (out of service), EMULSIFIER PUMP - P6 (no breaker / blank per field check).
Breakers
Pos | Poles | Trip (A) | Frame/Model | Conductor | Load served | Status | Verified | Notes
1 | 3 | 150 | HJA36150 / Square D PowerPact HJ 150 | TBD | SP-1 & SP-2 | active | VERIFIED | engraved label SP-1 & SP-2; PowerPact HJA36150 confirmed by photo
3 | TBD | 40 | TBD | TBD | TANK 11 AGITATOR | active | ASSUMED | orange label TANK 11 AGITATOR; trip 40 A per handwritten schedule; pole count not yet verified
5 | TBD | 40 | TBD | TBD | SOAP PUMP 1 (P7) | active | ASSUMED | orange label SOAP PUMP 1 - P7; engraved SOAP PUMP #1; trip 40 A per handwritten
7 | 3 | 100 | HJA36100 / Square D PowerPact HJ 150 | TBD | TANK #3 HEAT | active | VERIFIED | engraved label TANK #3 HEAT; PowerPact HJA36100 confirmed by photo
9 | 1 | 20 | Square D | TBD | SOAP PUMP #2 (P-number TBD) | active | VERIFIED | engraved label SOAP PUMP #2; orange label SOAP PUMP 2 - P? (P-number digit not legible in photo — I previously wrote P8 without confirming it; verify in field); close-up photo shows single-pole 20 A handle. 20 A trip confirmed by user.
11 | TBD | TBD | TBD | TBD | TBD | removed | ASSUMED | marked removed / not in use; handwritten note '15K' meaning unclear (per user, not in use)
13 | TBD | 70 | TBD | TBD | RACK 1 LOAD PUMP (P3) | active | ASSUMED | orange label RACK 1 PUMP - P3; engraved LOAD PUMP; 70 A per handwritten; FA34070 photo on file but position not yet pinned
15 | TBD | 70 | TBD | TBD | TBD | removed | ASSUMED | removed; handwritten notes 'AC pump 50 A' as the prior load on this position
17 | TBD | 70 | TBD | TBD | TBD | removed | ASSUMED | removed per handwritten schedule
19 | TBD | TBD | TBD | TBD | TBD | spare | ASSUMED | blank per handwritten schedule
21 | TBD | 30 | TBD | TBD | EPR-1 (P11) | removed | ASSUMED | engraved label EPR-1; orange label EPR-1 PUMP - P11; X'd out on handwritten schedule = removed
2 | TBD | 50 | TBD | TBD | TBD | removed | ASSUMED | removed per handwritten schedule (50 A frame size noted)
4 | 3 | 50 | FA34050 / Square D FA, series 2 | TBD | RACK 2 PUMP (P4) | active | VERIFIED | orange label RACK 2 PUMP - P4; FA34050 50 A 3-pole confirmed by photo
6 | TBD | TBD | TBD | TBD | TBD | spare | ASSUMED | blank per user
8 | TBD | TBD | TBD | TBD | TBD | spare | ASSUMED | blank
10 | TBD | TBD | TBD | TBD | TBD | spare | ASSUMED | blank
12 | TBD | TBD | TBD | TBD | TBD | spare | ASSUMED | blank
14 | TBD | TBD | TBD | TBD | TBD | spare | ASSUMED | blank
16 | TBD | TBD | TBD | TBD | TBD | spare | ASSUMED | blank
18 | TBD | TBD | TBD | TBD | DIESEL PUMP #2 (was, P5) | removed | ASSUMED | engraved label '#2 DIESEL PUMP'; orange label DIESEL PUMP - P5 nearby (pairing with this position assumed, not confirmed); removed per handwritten
20 | TBD | TBD | TBD | TBD | TBD | spare | ASSUMED | blank
22 | TBD | 60 | TBD | TBD | UNLOADING PUMP 1 (was, P1) | removed | ASSUMED | orange label UNLOADING PUMP - P1; engraved UNLOADING PUMP; 60 A frame; removed per handwritten
TBD-PRODUCTION-PUMP-P2 | TBD | TBD | TBD | TBD | PRODUCTION PUMP (P2) | active | ASSUMED | orange label PRODUCTION PUMP - P2 on panel door; position and trip TBD
TBD-MILL-AIR-COMP | TBD | TBD | TBD | TBD | MILL #2 AIR COMPRESSOR (M11) | out | ASSUMED | orange label MILL - M11 AIR COMPRESSOR; engraved MILL #2 AIR COMP.; user reports not in use; position TBD
TBD-EMULSIFIER-P6 | TBD | TBD | TBD | TBD | EMULSIFIER PUMP (P6) | removed | ASSUMED | orange label EMULSIFIER PUMP - P6; user reports BLANK at panel (no breaker); position TBD